## Sheet1
[5 empty] | Overhead Line Configurations (Config.) | [31 empty] | Node Voltage pu |  |  |  | Spot Loads | [8 empty] | Shunt Capacitors
Line Segment Data | [15 empty] | Distributed Loads | [5 empty] | Xendee Code Word for Wires | [18 empty] | Load |  |  | Ph-1 | Ph-1 | Ph-2 | Ph-2 | Ph-3 | Ph-4 | Ph-A | Ph-B | Ph-C
Node A | Node B | Length(ft.) | Length(km) | Config. | Phasing | Load |  |  | Phase | Phase A |  | Phase B |  | Phase C |  | Ph-1 |  | Ph-2 |  | Ph-3 |  | Neutral |  | Neutral |  | Overhead Line Spacings | [10 empty] | Node | A-N | B-N | C-N | Model | Connection | Model | kW | kVAr | kW | kVAr | kW | kVAr | kVAr | kVAr | kVAr
[6 empty] | Model | Connection | Model | ACSR | x | y | x | y | x | y | kW | kVAr | kW | kVAr | kW | kVAr | ACSR |  | x | y | Spacing ID | Type | [9 empty] | 800 | 1.05 | 1.05 | 1.05
800 | 802 | 2580 | 0.78639 | 300 | B A C N |  |  | ACSR: 1/0; x: -1.5; y: 28; x: -4; y: 28; x: 3; y: 28; ACSR: 1/0 | IEEE 8 | 0 | 24 | 500 | Three-Phase, 4 wire | [9 empty] | 802 | 1.047 | 1.048 | 1.048
802 | 806 | 1730 | 0.52731 | 300 | B A C N | Y-PQ | Wye | Constant kW and kVAr | 1/0 | -1.5 | 28 | -4 | 28 | 3 | 28 | 0(1e-6) | 0 | 30 | 15 | 25 | 14 | 1/0 | IEEE 8 | 0 | 24 | 500 | Three-Phase, 4 wire | [9 empty] | 806 | 1.046 | 1.047 | 1.047
806 | 808 | 32230 | 9.8238 | 300 | B A C N |  |  | ACSR: 1/0; x: -1.5; y: 28; x: -4; y: 28; x: 3; y: 28; ACSR: 1/0 | IEEE 8 | 0 | 24 | 500 | Three-Phase, 4 wire | [9 empty] | 808 | 1.014 | 1.03 | 1.029
808 | 810 | 5804 | 1.7691 | 303 | B N | Y-I | Wye | Model: Constant Current; ACSR: #4 6/1; x: -0.5; y: 29; kW: 16; kVAr: 8; ACSR: #4 6/1 | IEEE 12 | 0 | 24 | 510 | Single-Phase, 2 wire | [9 empty] | 810 |  | 1.029
808 | 812 | 37500 | 11.4301 | 300 | B A C N |  |  | ACSR: 1/0; x: -1.5; y: 28; x: -4; y: 28; x: 3; y: 28; ACSR: 1/0 | IEEE 8 | 0 | 24 | 500 | Three-Phase, 4 wire | [9 empty] | 812 | 0.9769 | 1.01 | 1.006
812 | 814 | 29730 | 9.0618 | 300 | B A C N |  |  | ACSR: 1/0; x: -1.5; y: 28; x: -4; y: 28; x: 3; y: 28; ACSR: 1/0 | IEEE 8 | 0 | 24 | 500 | Three-Phase, 4 wire | [9 empty] | 814 | 0.9474 | 0.9943 | 0.9887
814 | 850 | 10 | 0.003048 | 301 | B A C N |  |  | ACSR: #2 6/1; x: -1.5; y: 28; x: -4; y: 28; x: 3; y: 28; ACSR: #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire | [9 empty] | 850 | 1.018 | 1.025 | 1.02
816 | 818 | 1710 | 0.52121 | 302 | A N |  |  | ACSR: #4 6/1; x: -0.5; y: 29; ACSR: #4 6/1 | IEEE 12 | 0 | 24 | 510 | Single-Phase, 2 wire | [9 empty] | 816 | 1.018 | 1.025 | 1.019
816 | 824 | 10210 | 3.112 | 301 | B A C N | D-I | Delta | Constant Current | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | 0 | 0 | 5 | 2 | 0 | 0 | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire | [9 empty] | 818 | 1.017
818 | 820 | 48150 | 14.6763 | 302 | A N | Y-Z | Wye | Model: Constant Impedance; ACSR: #4 6/1; x: -0.5; y: 29; kW: 34; kVAr: 17; ACSR: #4 6/1 | IEEE 12 | 0 | 24 | 510 | Single-Phase, 2 wire | [9 empty] | 820 | 0.9941
820 | 822 | 13740 | 4.188 | 302 | A N | Y-PQ | Wye | Model: Constant kW and kVAr; ACSR: #4 6/1; x: -0.5; y: 29; kW: 135; kVAr: 70; ACSR: #4 6/1 | IEEE 12 | 0 | 24 | 510 | Single-Phase, 2 wire | [9 empty] | 822 | 0.9912
824 | 826 | 3030 | 0.92356 | 303 | B N | Y-I | Wye | Model: Constant Current; ACSR: #4 6/1; x: -0.5; y: 29; kW: 40; kVAr: 20; ACSR: #4 6/1 | IEEE 12 | 0 | 24 | 510 | Single-Phase, 2 wire | [9 empty] | 824 | 1.009 | 1.016 | 1.011
824 | 828 | 840 | 0.25604 | 301 | B A C N | Y-PQ | Wye | Constant kW and kVAr | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | 0(1e-6) | 0 | 0(1e-6) | 0 | 4 | 2 | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire | ACSR: Aluminum conductor Steel Reinforced | [8 empty] | 826 |  | 1.016
828 | 830 | 20440 | 6.2302 | 301 | B A C N | Y-PQ | Wye | Constant kW and kVAr | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | 7 | 3 | 0(1e-6) | 0 | 0(1e-6) | 0 | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | Transformer Data | [7 empty] | 828 | 1.008 | 1.015 | 1.01
830 | 854 | 520 | 0.1585 | 301 | B A C N |  |  | ACSR: #2 6/1; x: -1.5; y: 28; x: -4; y: 28; x: 3; y: 28; ACSR: #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | kVA | kV-high | kV-low | R - % | X - % |  |  |  | 830 | 0.9903 | 0.998 | 0.9929 | D-Z | Delta | Constant Impedance | 10 | 5 | 10 | 5 | 25 | 10
832 | 858 | 4900 | 1.4935 | 301 | B A C N | D-Z | Delta | Constant Impedance | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | 7 | 3 | 2 | 1 | 6 | 3 | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire | Substation: | 2500 | 69 - D | 24.9 -Gr. W | 1 | 8 |  |  |  | 854 | 0.9898 | 0.9976 | 0.9925
832 | 888 | 0 | 0 | XFM-1 | [23 empty] | XFM -1: | 500 | 24.9 - Gr.W | 4.16 - Gr. W | 1.9 | 4.08 |  |  |  | 852 | 0.9589 | 0.9678 | 0.9627
834 | 860 | 2020 | 0.6157 | 301 | B A C N | D-Z | Delta | Constant Impedance | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | 16 | 8 | 20 | 10 | 110 | 55 | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire | [9 empty] | 832 | 1.037 | 1.034 | 1.035
834 | 842 | 280 | 0.085345 | 301 | B A C N |  |  | ACSR: #2 6/1; x: -1.5; y: 28; x: -4; y: 28; x: 3; y: 28; ACSR: #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire | [9 empty] | 858 | 1.034 | 1.032 | 1.033
836 | 840 | 860 | 0.26213 | 301 | B A C N | D-I | Delta |  | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | 18 | 9 | 22 | 11 | 0(1e-6) | 0 | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | Regulator Data | [7 empty] | 834 | 1.032 | 1.029 | 1.03
836 | 862 | 280 | 0.085345 | 301 | B A C N |  |  | Constant Current | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | [6 empty] | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | Regulator ID: |  | 1 |  |  | 2 |  |  | 842 | 1.032 | 1.029 | 1.03
842 | 844 | 1350 | 0.41149 | 301 | B A C N | Y-PQ | Wye | Constant kW and kVAr | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | 9 | 5 | 0(1e-6) | 0 | 0(1e-6) | 0 | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | Line Segment: |  | 814 - 850 |  |  | 852 - 832 |  |  | 844 | 1.031 | 1.029 | 1.03 | Y-Z | Wye | Constant Impedance | 135 | 105 | 135 | 105 | 135 | 105 | 100 | 100 | 100
844 | 846 | 3640 | 1.1095 | 301 | B A C N | Y-PQ | Wye | Constant kW and kVAr | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | 0(1e-6) | 0 | 25 | 12 | 20 | 11 | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | Location: |  | 814 |  |  | 852 |  |  | 846 | 1.032 | 1.029 | 1.03
846 | 848 | 530 | 0.16155 | 301 | B A C N | Y-PQ | Wye | Constant kW and kVAr | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | 0(1e-6) | 0 | 23 | 11 | 0(1e-6) | 0 | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | Phases: |  | A - B -C |  |  | A - B -C |  |  | 848 | 1.032 | 1.029 | 1.03 | D-PQ | Delta | Constant kW and kVAr | 20 | 16 | 20 | 16 | 20 | 16 | 150 | 150 | 150
850 | 816 | 310 | 0.094489 | 301 | B A C N |  |  | ACSR: #2 6/1; x: -1.5; y: 28; x: -4; y: 28; x: 3; y: 28; ACSR: #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | Connection: |  | 3-Ph,LG |  |  | 3-Ph,LG |  |  | 860 | 1.031 | 1.029 | 1.03 | Y-PQ | Wye | Constant kW and kVAr | 20 | 16 | 20 | 16 | 20 | 16
852 | 832 | 10 | 0.003048 | 301 | B A C N |  |  | ACSR: #2 6/1; x: -1.5; y: 28; x: -4; y: 28; x: 3; y: 28; ACSR: #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | Monitoring Phase: |  | A-B-C |  |  | A-B-C |  |  | 836 | 1.031 | 1.028 | 1.03
854 | 856 | 23330 | 7.1111 | 303 | B N | Y-PQ | Wye | Model: Constant kW and kVAr; x: -0.5; y: 29; kW: 4; kVAr: 2; ACSR: #4 6/1 | IEEE 12 | 0 | 24 | 510 | Single-Phase, 2 wire |  | Bandwidth: |  | 2.0 volts |  |  | 2.0 volts |  |  | 840 | 1.031 | 1.029 | 1.03 | Y-I | Wye | Constant Current | 9 | 7 | 9 | 7 | 9 | 7
854 | 852 | 36830 | 11.2259 | 301 | B A C N |  |  | ACSR: #2 6/1; x: -1.5; y: 28; x: -4; y: 28; x: 3; y: 28; ACSR: #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | PT Ratio: |  | 120 |  |  | 120 |  |  | 862 | 1.031 | 1.029 | 1.03
858 | 864 | 1620 | 0.49378 | 302 | A N | Y-PQ | Wye | Model: Constant kW and kVAr; ACSR: #4 6/1; x: -0.5; y: 29; kW: 2; kVAr: 1; ACSR: #4 6/1 | IEEE 12 | 0 | 24 | 510 | Single-Phase, 2 wire |  | Primary CT Rating: |  | 100 |  |  | 100 |  |  | 838 |  | 1.028
858 | 834 | 5830 | 1.777 | 301 | B A C N | D-PQ | Delta | Constant kW and kVAr | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | 4 | 2 | 15 | 8 | 13 | 7 | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | Compensator Settings: |  | Ph-A | Ph-B | Ph-C | Ph-A | Ph-B | Ph-C | 864 | 1.034
860 | 836 | 2680 | 0.81687 | 301 | B A C N | D-PQ | Delta | Constant kW and kVAr | #2 6/1 | -1.5 | 28 | -4 | 28 | 3 | 28 | 30 | 15 | 10 | 6 | 42 | 22 | #2 6/1 | IEEE 11 | 0 | 24 | 500 | Three-Phase, 4 wire |  | R - Setting: |  | 2.7 | 2.7 | 2.7 | 2.5 | 2.5 | 2.5 | 888 | 0.9961 | 1.004 | 0.9962
862 | 838 | 4860 | 1.4813 | 304 | B N | Y-PQ | Wye | Model: Constant kW and kVAr; ACSR: #2 6/1; x: -0.5; y: 29; kW: 28; kVAr: 14; ACSR: #2 6/1 | IEEE 11 | 0 | 24 | 510 | Single-Phase, 2 wire |  | X - Setting: |  | 1.6 | 1.6 | 1.6 | 1.5 | 1.5 | 1.5 | 890 | 0.9134 | 0.9294 | 0.9138 | D-I | Delta | Constant Current | 150 | 75 | 150 | 75 | 150 | 75
888 | 890 | 10560 | 3.2187 | 300 | B A C N |  |  | ACSR: 1/0; x: -1.5; y: 28; x: -4; y: 28; x: 3; y: 28; ACSR: 1/0 | IEEE 8 | 0 | 24 | 500 | Three-Phase, 4 wire |  | Volltage Level: |  | 122 | 122 | 122 | 124 | 124 | 124 | 856 |  | 0.9976
[8 empty] | y: Total; kW: #VALUE!; kVAr: 133; kW: #VALUE!; kVAr: 120; kW: #VALUE!; kVAr: 114 |  |  |  | (505) | Two-Phase, 3 wire | [12 empty] | Total |  |  |  | 344 | 224 | 344 | 224 | 359 | 229 | 250 | 250 | 250
[25 empty] | Underground Line Spacings | (515) | Three-Phase, 3 Cable
[26 empty] | (520) | Single-Phase, 2 Cable
This feeder is an actual feeder located in Arizona.
The feeder’s nominal voltage is 24.9 kV. It is characterized by:
1. Very long and lightly loaded overhead transmission lines
2. Two in-line regulators required to maintain a good voltage profile
3. An in-line transformer reducing the voltage to 4.16 kV for a short section of the feeder
4. 24 unbalanced loading with both “spot” and “distributed” loads. Distributed loads are assumed to be connected at the center of the line segment
5. Shunt capacitors
Because of the length of the feeder and the unbalanced loading it can have a convergence problem.

## Sheet2
R_300 | 1.3368 | 0.2101 | 0.213 | X_300 | 1.3343 | 0.5779 | 0.5015 | B_300 | 5.335 | -1.5313 | -0.9943 | L_300 | 0.0022034 | 0.0003463 | 0.00035108 | C_300
ohms/mi | 0.2101 | 1.3238 | 0.2066 |  | 0.5779 | 1.3569 | 0.4591 | micro-Simens/mi | -1.5313 | 5.0979 | -0.6212 |  | 0.0003463 | 0.0021819 | 0.00034053
| 0.213 | 0.2066 | 1.3294 |  | 0.5015 | 0.4591 | 1.3471 |  | -0.9943 | -0.6212 | 4.888 |  | 0.00035108 | 0.00034053 | 0.0021912
R_301 | 1.93 | 0.2327 | 0.2359 | X_301 | 1.4115 | 0.6442 | 0.5691 | B_301 | 5.1207 | -1.4364 | -0.9402 | L_301 |  |  |  | C_301
| 0.2327 | 1.9157 | 0.2288 |  | 0.6442 | 1.4281 | 0.5238 |  | -1.4364 | 4.9055 | -0.5951
| 0.2359 | 0.2288 | 1.9219 |  | 0.5691 | 0.5238 | 1.4209 |  | -0.9402 | -0.5951 | 4.7154
R_302 | 2.7995 | 0 | 0 | X_302 | 1.4855 | 0 | 0 | B_302 | 4.2251 | 0 | 0 | L_302 |  | 0 | 0 | C_302 |  | 0 | 0
| 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
| 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
R_303 | 0 | 0 | 0 | X_303 | 0 | 0 | 0 | B_303 | 0 | 0 | 0 | L_303 | 0 | 0 | 0 | C_303 | 0 | 0 | 0
| 0 | 2.7995 | 0 |  | 0 | 1.4855 | 0 |  | 0 | 4.2251 | 0 |  | 0 |  | 0 |  | 0 |  | 0
| 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
R_304 | 0 | 0 | 0 | X_304 | 0 | 0 | 0 | B_304 | 0 | 0 | 0 | L_304 | 0 | 0 | 0 | C_304 | 0 | 0 | 0
| 0 | 1.9217 | 0 |  | 0 | 1.4212 | 0 |  | 0 | 4.3637 | 0 |  | 0 |  | 0 |  | 0 |  | 0
| 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
[12 empty] | L=X/mi2km/2/pi/60 |  |  |  | C=B/mi2km*ms2F
ft2km | 0.0003048
mi2km | 1.6093
ms2F | 2.6526e-09 | 1/(w*1e-6)
inf | infinite
1/0/0m |  |  | Distributed Loads | Spot Loads
|  |  | 802-806 | 830
w=2*pi*f |  |  | 808-810 | 844
R=r/mi2km |  |  | 816-824 | 848
X=x/mi2km |  |  | 816-820 | 860
B=b/mi2km |  |  | 820-822 | 840
L=X/w |  |  | 824-826 | 890
C=B*ms2F |  |  | 824-828
|  |  | 828-830 | V
|  |  | 832-858 | Pa
|  |  | 834-860 | Pp
|  |  | 836-840 | Pn
842-844
844-846
846-848
854-856
858-864
858-834
860-836
862-838
V
Pa
Pp
Pn

## Sheet3
800-802 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  | rate | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 800-802 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
BACN | 0.48864 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.65321 | 0.64686 | 0.64959 | 0.10266 | 0.10408 | 0.10095 | 2.6069 | 2.491 | 2.3885 | -0.74825 | -0.30354 | -0.48585
|  | 0.5015 | 0.4591 | 0.5779 | 0.213 | 0.2066 | 0.2101 | 1.3471 | 1.3569 | 1.3343 | 1.3294 | 1.3238 | 1.3368 | -0.9943 | -0.6212 | -1.5313 | 4.888 | 5.0979 | 5.335 | 0.48864 | 2580 | 0.00018939 | 0.24505 | 0.22433 | 0.28238 | 0.10408 | 0.10095 | 0.10266 | 0.65824 | 0.66303 | 0.65199 | 0.64959 | 0.64686 | 0.65321 | -0.48585 | -0.30354 | -0.74825 | 2.3885 | 2.491 | 2.6069 |  | 0.65199 | 0.66303 | 0.65824 | 0.28238 | 0.24505 | 0.22433
802-806 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 802-806 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.081913 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.43801 | 0.43375 | 0.43558 | 0.06884 | 0.06979 | 0.067693 | 1.748 | 1.6703 | 1.6016 | -0.50173 | -0.20354 | -0.32578
| 0.24574 | 0.5015 | 0.4591 | 0.5779 | 0.213 | 0.2066 | 0.2101 | 1.3471 | 1.3569 | 1.3343 | 1.3294 | 1.3238 | 1.3368 | -0.9943 | -0.6212 | -1.5313 | 4.888 | 5.0979 | 5.335 | 0.32765 | 1730 | 0.00018939 | 0.16432 | 0.15043 | 0.18935 | 0.06979 | 0.067693 | 0.06884 | 0.44138 | 0.44459 | 0.43719 | 0.43558 | 0.43375 | 0.43801 | -0.32578 | -0.20354 | -0.50173 | 1.6016 | 1.6703 | 1.748 |  | 0.43719 | 0.44459 | 0.44138 | 0.18935 | 0.16432 | 0.15043
806-808 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 806-808 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 6.1042 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 8.1601 | 8.0807 | 8.1149 | 1.2825 | 1.3002 | 1.2611 | 32.5657 | 31.1184 | 29.8372 | -9.3473 | -3.7919 | -6.0694
|  | 0.5015 | 0.4591 | 0.5779 | 0.213 | 0.2066 | 0.2101 | 1.3471 | 1.3569 | 1.3343 | 1.3294 | 1.3238 | 1.3368 | -0.9943 | -0.6212 | -1.5313 | 4.888 | 5.0979 | 5.335 | 6.1042 | 32230 | 0.00018939 | 3.0612 | 2.8024 | 3.5276 | 1.3002 | 1.2611 | 1.2825 | 8.2229 | 8.2827 | 8.1448 | 8.1149 | 8.0807 | 8.1601 | -6.0694 | -3.7919 | -9.3473 | 29.8372 | 31.1184 | 32.5657 |  | 8.1448 | 8.2827 | 8.2229 | 3.5276 | 3.0612 | 2.8024
808-812 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 808-812 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 7.1023 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 9.4943 | 9.402 | 9.4418 | 1.4922 | 1.5128 | 1.4673 | 37.8906 | 36.2067 | 34.7159 | -10.8757 | -4.4119 | -7.0618
|  | 0.5015 | 0.4591 | 0.5779 | 0.213 | 0.2066 | 0.2101 | 1.3471 | 1.3569 | 1.3343 | 1.3294 | 1.3238 | 1.3368 | -0.9943 | -0.6212 | -1.5313 | 4.888 | 5.0979 | 5.335 | 7.1023 | 37500 | 0.00018939 | 3.5618 | 3.2607 | 4.1044 | 1.5128 | 1.4673 | 1.4922 | 9.5675 | 9.6371 | 9.4766 | 9.4418 | 9.402 | 9.4943 | -7.0618 | -4.4119 | -10.8757 | 34.7159 | 36.2067 | 37.8906 |  | 9.4766 | 9.6371 | 9.5675 | 4.1044 | 3.5618 | 3.2607
812-814 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 812-814 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 5.6307 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 7.5271 | 7.4539 | 7.4854 | 1.183 | 1.1993 | 1.1633 | 30.0397 | 28.7047 | 27.5228 | -8.6223 | -3.4978 | -5.5986
|  | 0.5015 | 0.4591 | 0.5779 | 0.213 | 0.2066 | 0.2101 | 1.3471 | 1.3569 | 1.3343 | 1.3294 | 1.3238 | 1.3368 | -0.9943 | -0.6212 | -1.5313 | 4.888 | 5.0979 | 5.335 | 5.6307 | 29730 | 0.00018939 | 2.8238 | 2.585 | 3.254 | 1.1993 | 1.1633 | 1.183 | 7.5851 | 7.6403 | 7.513 | 7.4854 | 7.4539 | 7.5271 | -5.5986 | -3.4978 | -8.6223 | 27.5228 | 28.7047 | 30.0397 |  | 7.513 | 7.6403 | 7.5851 | 3.254 | 2.8238 | 2.585
888-890 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 888-890 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 2 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 2.6736 | 2.6476 | 2.6588 | 0.4202 | 0.426 | 0.4132 | 10.67 | 10.1958 | 9.776 | -3.0626 | -1.2424 | -1.9886
|  | 0.5015 | 0.4591 | 0.5779 | 0.213 | 0.2066 | 0.2101 | 1.3471 | 1.3569 | 1.3343 | 1.3294 | 1.3238 | 1.3368 | -0.9943 | -0.6212 | -1.5313 | 4.888 | 5.0979 | 5.335 | 2 | 10560 | 0.00018939 | 1.003 | 0.9182 | 1.1558 | 0.426 | 0.4132 | 0.4202 | 2.6942 | 2.7138 | 2.6686 | 2.6588 | 2.6476 | 2.6736 | -1.9886 | -1.2424 | -3.0626 | 9.776 | 10.1958 | 10.67 |  | 2.6686 | 2.7138 | 2.6942 | 1.1558 | 1.003 | 0.9182
814-850 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 814-850 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
BACN | 0.001894 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.0036554 | 0.0036283 | 0.0036401 | 0.00044073 | 0.00044679 | 0.00043335 | 0.0096986 | 0.009291 | 0.008931 | -0.0027205 | -0.0011271 | -0.0017807
|  | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.001894 | 10 | 0.0001894 | 0.0010779 | 0.00099208 | 0.0012201 | 0.00044679 | 0.00043335 | 0.00044073 | 0.0026912 | 0.0027048 | 0.0026734 | 0.0036401 | 0.0036283 | 0.0036554 | -0.0017807 | -0.0011271 | -0.0027205 | 0.008931 | 0.009291 | 0.0096986 |  | 0.0026734 | 0.0027048 | 0.0026912 | 0.0012201 | 0.0010779 | 0.00099208
850-816 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 850-816 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.058712 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.11331 | 0.11247 | 0.11284 | 0.013662 | 0.01385 | 0.013433 | 0.30065 | 0.28801 | 0.27685 | -0.084334 | -0.03494 | -0.055201
|  | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.058712 | 310 | 0.00018939 | 0.033413 | 0.030753 | 0.037822 | 0.01385 | 0.013433 | 0.013662 | 0.083424 | 0.083847 | 0.082872 | 0.11284 | 0.11247 | 0.11331 | -0.055201 | -0.03494 | -0.084334 | 0.27685 | 0.28801 | 0.30065 |  | 0.082872 | 0.083847 | 0.083424 | 0.037822 | 0.033413 | 0.030753
816-824 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 816-824 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.48343 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 3.7321 | 3.7044 | 3.7164 | 0.44997 | 0.45616 | 0.44243 | 9.902 | 9.4858 | 9.1182 | -2.7776 | -1.1508 | -1.8181
| 1.4503 | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 1.9337 | 10210 | 0.00018939 | 1.1005 | 1.0129 | 1.2457 | 0.45616 | 0.44243 | 0.44997 | 2.7476 | 2.7615 | 2.7294 | 3.7164 | 3.7044 | 3.7321 | -1.8181 | -1.1508 | -2.7776 | 9.1182 | 9.4858 | 9.902 |  | 2.7294 | 2.7615 | 2.7476 | 1.2457 | 1.1005 | 1.0129
824-828 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 824-828 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.11932 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.30705 | 0.30477 | 0.30576 | 0.03702 | 0.03753 | 0.0364 | 0.81466 | 0.78042 | 0.75018 | -0.22852 | -0.094675 | -0.14958
| 0.039773 | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.15909 | 840 | 0.00018939 | 0.090539 | 0.083332 | 0.10249 | 0.03753 | 0.0364 | 0.03702 | 0.22605 | 0.2272 | 0.22456 | 0.30576 | 0.30477 | 0.30705 | -0.14958 | -0.094675 | -0.22852 | 0.75018 | 0.78042 | 0.81466 |  | 0.22456 | 0.2272 | 0.22605 | 0.10249 | 0.090539 | 0.083332
828-830 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 828-830 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.9678 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 7.4714 | 7.4161 | 7.4401 | 0.90083 | 0.91322 | 0.88573 | 19.8233 | 18.9902 | 18.2543 | -5.5606 | -2.3038 | -3.6397
| 2.9034 | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 3.8712 | 20440 | 0.00018939 | 2.2031 | 2.0277 | 2.4938 | 0.91322 | 0.88573 | 0.90083 | 5.5006 | 5.5285 | 5.4642 | 7.4401 | 7.4161 | 7.4714 | -3.6397 | -2.3038 | -5.5606 | 18.2543 | 18.9902 | 19.8233 |  | 5.4642 | 5.5285 | 5.5006 | 2.4938 | 2.2031 | 2.0277
830-854 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 830-854 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.098485 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.19008 | 0.18867 | 0.18928 | 0.022917 | 0.023233 | 0.022533 | 0.50431 | 0.48312 | 0.4644 | -0.14146 | -0.058608 | -0.092596
|  | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.098485 | 520 | 0.00018939 | 0.056048 | 0.051586 | 0.063444 | 0.023233 | 0.022533 | 0.022917 | 0.13994 | 0.14065 | 0.13901 | 0.18928 | 0.18867 | 0.19008 | -0.092596 | -0.058608 | -0.14146 | 0.4644 | 0.48312 | 0.50431 |  | 0.13901 | 0.14065 | 0.13994 | 0.063444 | 0.056048 | 0.051586
854-852 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 854-852 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 6.9754 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 13.4625 | 13.3627 | 13.406 | 1.6232 | 1.6455 | 1.596 | 35.7188 | 34.2177 | 32.8917 | -10.0194 | -4.151 | -6.5583
|  | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 6.9754 | 36830 | 0.00018939 | 3.9697 | 3.6537 | 4.4935 | 1.6455 | 1.596 | 1.6232 | 9.9113 | 9.9615 | 9.8457 | 13.406 | 13.3627 | 13.4625 | -6.5583 | -4.151 | -10.0194 | 32.8917 | 34.2177 | 35.7188 |  | 9.8457 | 9.9615 | 9.9113 | 4.4935 | 3.9697 | 3.6537
852-832 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 852-832 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.001894 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.0036554 | 0.0036283 | 0.0036401 | 0.00044073 | 0.00044679 | 0.00043335 | 0.0096986 | 0.009291 | 0.008931 | -0.0027205 | -0.0011271 | -0.0017807
|  | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.001894 | 10 | 0.0001894 | 0.0010779 | 0.00099208 | 0.0012201 | 0.00044679 | 0.00043335 | 0.00044073 | 0.0026912 | 0.0027048 | 0.0026734 | 0.0036401 | 0.0036283 | 0.0036554 | -0.0017807 | -0.0011271 | -0.0027205 | 0.008931 | 0.009291 | 0.0096986 |  | 0.0026734 | 0.0027048 | 0.0026912 | 0.0012201 | 0.0010779 | 0.00099208
832-858 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 832-858 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.23201 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 1.7911 | 1.7778 | 1.7836 | 0.21595 | 0.21892 | 0.21233 | 4.7522 | 4.5525 | 4.376 | -1.333 | -0.55227 | -0.87253
| 0.69602 | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.92803 | 4900 | 0.00018939 | 0.52814 | 0.4861 | 0.59784 | 0.21892 | 0.21233 | 0.21595 | 1.3186 | 1.3253 | 1.3099 | 1.7836 | 1.7778 | 1.7911 | -0.87253 | -0.55227 | -1.333 | 4.376 | 4.5525 | 4.7522 |  | 1.3099 | 1.3253 | 1.3186 | 0.59784 | 0.52814 | 0.4861
858-834 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 858-834 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.27604 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 2.131 | 2.1153 | 2.1221 | 0.25694 | 0.26047 | 0.25263 | 5.6541 | 5.4165 | 5.2066 | -1.586 | -0.65709 | -1.0381
| 0.82812 | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 1.1042 | 5830 | 0.00018939 | 0.62838 | 0.57836 | 0.7113 | 0.26047 | 0.25263 | 0.25694 | 1.5689 | 1.5769 | 1.5585 | 2.1221 | 2.1153 | 2.131 | -1.0381 | -0.65709 | -1.586 | 5.2066 | 5.4165 | 5.6541 |  | 1.5585 | 1.5769 | 1.5689 | 0.7113 | 0.62838 | 0.57836
834-842 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 834-842 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.05303 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.10235 | 0.10159 | 0.10192 | 0.01234 | 0.01251 | 0.012133 | 0.27155 | 0.26014 | 0.25006 | -0.076172 | -0.031558 | -0.049859
|  | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.05303 | 280 | 0.00018939 | 0.030179 | 0.027777 | 0.034162 | 0.01251 | 0.012133 | 0.01234 | 0.07535 | 0.075732 | 0.074852 | 0.10192 | 0.10159 | 0.10235 | -0.049859 | -0.031558 | -0.076172 | 0.25006 | 0.26014 | 0.27155 |  | 0.074852 | 0.075732 | 0.07535 | 0.034162 | 0.030179 | 0.027777
842-844 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 842-844 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.06392 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.49346 | 0.48981 | 0.49139 | 0.059497 | 0.060315 | 0.0585 | 1.3093 | 1.2542 | 1.2056 | -0.36726 | -0.15216 | -0.24039
| 0.19176 | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.25568 | 1350 | 0.00018939 | 0.14551 | 0.13393 | 0.16471 | 0.060315 | 0.0585 | 0.059497 | 0.3633 | 0.36514 | 0.36089 | 0.49139 | 0.48981 | 0.49346 | -0.24039 | -0.15216 | -0.36726 | 1.2056 | 1.2542 | 1.3093 |  | 0.36089 | 0.36514 | 0.3633 | 0.16471 | 0.14551 | 0.13393
844-846 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 844-846 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.51704 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 1.3305 | 1.3207 | 1.3249 | 0.16042 | 0.16263 | 0.15773 | 3.5302 | 3.3818 | 3.2508 | -0.99024 | -0.41026 | -0.64817
| 0.17235 | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.68939 | 3640 | 0.00018939 | 0.39233 | 0.3611 | 0.44411 | 0.16263 | 0.15773 | 0.16042 | 0.97956 | 0.98452 | 0.97308 | 1.3249 | 1.3207 | 1.3305 | -0.64817 | -0.41026 | -0.99024 | 3.2508 | 3.3818 | 3.5302 |  | 0.97308 | 0.98452 | 0.97956 | 0.44411 | 0.39233 | 0.3611
846-848 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 846-848 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.025095 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.19373 | 0.1923 | 0.19292 | 0.023358 | 0.023679 | 0.022967 | 0.51401 | 0.49241 | 0.47333 | -0.14418 | -0.059736 | -0.094376
| 0.075284 | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.10038 | 530 | 0.00018939 | 0.057126 | 0.052579 | 0.064664 | 0.023679 | 0.022967 | 0.023358 | 0.14263 | 0.14335 | 0.14168 | 0.19292 | 0.1923 | 0.19373 | -0.094376 | -0.059736 | -0.14418 | 0.47333 | 0.49241 | 0.51401 |  | 0.14168 | 0.14335 | 0.14263 | 0.064664 | 0.057126 | 0.052579
834-860 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 834-860 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.095644 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.73837 | 0.7329 | 0.73527 | 0.089025 | 0.09025 | 0.087533 | 1.9591 | 1.8767 | 1.804 | -0.54953 | -0.22767 | -0.3597
| 0.28693 | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.38258 | 2020 | 0.00018939 | 0.21772 | 0.20039 | 0.24646 | 0.09025 | 0.087533 | 0.089025 | 0.5436 | 0.54636 | 0.54001 | 0.73527 | 0.7329 | 0.73837 | -0.3597 | -0.22767 | -0.54953 | 1.804 | 1.8767 | 1.9591 |  | 0.54001 | 0.54636 | 0.5436 | 0.24646 | 0.21772 | 0.20039
860-836 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 860-836 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.12689 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.97962 | 0.97236 | 0.97551 | 0.11811 | 0.11974 | 0.11613 | 2.5991 | 2.4899 | 2.3934 | -0.72908 | -0.30206 | -0.47722
| 0.38068 | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.50758 | 2680 | 0.00018939 | 0.28886 | 0.26587 | 0.32698 | 0.11974 | 0.11613 | 0.11811 | 0.72121 | 0.72487 | 0.71644 | 0.97551 | 0.97236 | 0.97962 | -0.47722 | -0.30206 | -0.72908 | 2.3934 | 2.4899 | 2.5991 |  | 0.71644 | 0.72487 | 0.72121 | 0.32698 | 0.28886 | 0.26587
836-840 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 836-840 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.04072 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.31436 | 0.31203 | 0.31304 | 0.037902 | 0.038423 | 0.037267 | 0.83405 | 0.799 | 0.76804 | -0.23396 | -0.096929 | -0.15314
| 0.12216 | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.16288 | 860 | 0.00018939 | 0.092694 | 0.085316 | 0.10493 | 0.038423 | 0.037267 | 0.037902 | 0.23143 | 0.23261 | 0.2299 | 0.31304 | 0.31203 | 0.31436 | -0.15314 | -0.096929 | -0.23396 | 0.76804 | 0.799 | 0.83405 |  | 0.2299 | 0.23261 | 0.23143 | 0.10493 | 0.092694 | 0.085316
836-862 | Length | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | Length |  |  | Zm_AC | Zm_BC | Zm_AB | Zm_AC | Zm_BC | Zm_AB | Z_C | Z_B | Z_A | Z_C | Z_B | Z_A | C_BC | C_AC | C_AB | C_CC | C_BB | C_AA | 836-862 | Z_A (ohm) | Z_B | Z_C | Zm_AB | Zm_AC | Zm_BC | C_AA (uF) | C_BB | C_CC | C_AB | C_AC | C_BC
| 0.05303 | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [9 empty] | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | Reactance j | Reactance j | Reactance j | Resistance | Resistance | Resistance | [7 empty] | 0.10235 | 0.10159 | 0.10192 | 0.01234 | 0.01251 | 0.012133 | 0.27155 | 0.26014 | 0.25006 | -0.076172 | -0.031558 | -0.049859
|  | 0.5691 | 0.5238 | 0.6442 | 0.2359 | 0.2288 | 0.2327 | 1.4209 | 1.4281 | 1.4115 | 1.9219 | 1.9157 | 1.93 | -0.9402 | -0.5951 | -1.4364 | 4.7154 | 4.9055 | 5.1207 | 0.05303 | 280 | 0.00018939 | 0.030179 | 0.027777 | 0.034162 | 0.01251 | 0.012133 | 0.01234 | 0.07535 | 0.075732 | 0.074852 | 0.10192 | 0.10159 | 0.10235 | -0.049859 | -0.031558 | -0.076172 | 0.25006 | 0.26014 | 0.27155 |  | 0.074852 | 0.075732 | 0.07535 | 0.034162 | 0.030179 | 0.027777
816-818 | 1710
AN
818-820 | 48150
820-822 | 13740
858-864 | 1620
808-810 | 5804
BN
824-826 | 3030
854-856 | 23330
862-838 | 4860
BN
832-888 | 0

## etc.
Shunt Capacitors |  |  |  |  | Overhead Line Configurations (Config.) |  |  |  |  | Xendee Code Word for Wires
Node | Ph-A | Ph-B | Ph-C |  | Config. | Phasing | Phase | Neutral | Spacing ID | ACSR 1/0 | IEEE 8
| kVAr | kVAr | kVAr |  |  |  | ACSR | ACSR |  | ACSR #2 6/1 | IEEE 11
844 | 100 | 100 | 100 |  | 300 | B A C N | 1/0 | 1/0 | 500 | ACSR #4 6/1 | IEEE 12
848 | 150 | 150 | 150 |  | 301 | B A C N | #2 6/1 | #2 6/1 | 500
Total | 250 | 250 | 250 |  | 302 | A N | #4 6/1 | #4 6/1 | 510
[5 empty] | 303 | B N | #4 6/1 | #4 6/1 | 510
[5 empty] | 304 | B N | #2 6/1 | #2 6/1 | 510 | Config. | Phasing | Phase A |  | Phase B |  | Phase C |  | Neutral
[12 empty] | x | y | x | y | x | y | x | y
[10 empty] | 300 | B A C N | -1.5 | 28 | -4 | 28 | 3 | 28 | 0 | 24
Spot Loads | [9 empty] | 301 | B A C N | -1.5 | 28 | -4 | 28 | 3 | 28 | 0 | 24
[10 empty] | 302 | A N | -0.5 | 29 |  |  |  |  | 0 | 24
Node | Load | Ph-1 | Ph-1 | Ph-2 | Ph-2 | Ph-3 | Ph-4 |  |  | 303 | B N |  |  | -0.5 | 29 |  |  | 0 | 24
| Model | kW | kVAr | kW | kVAr | kW | kVAr |  |  | 304 | B N |  |  | -0.5 | 29 |  |  | 0 | 24
860 | Y-PQ | 20 | 16 | 20 | 16 | 20 | 16
840 | Y-I | 9 | 7 | 9 | 7 | 9 | 7
844 | Y-Z | 135 | 105 | 135 | 105 | 135 | 105
848 | D-PQ | 20 | 16 | 20 | 16 | 20 | 16
890 | D-I | 150 | 75 | 150 | 75 | 150 | 75
830 | D-Z | 10 | 5 | 10 | 5 | 25 | 10
Total |  | 344 | 224 | 344 | 224 | 359 | 229
Transformer Data
| kVA | kV-high | kV-low | R - % | X - %
Substation: | 2500 | 69 - D | 24.9 -Gr. W | 1 | 8
XFM -1 | 500 | 24.9 - Gr.W | 4.16 - Gr. W | 1.9 | 4.08

## distributed load data
Distributed Loads
Node | Node | Load | Ph-1 | Ph-1 | Ph-2 | Ph-2 | Ph-3 | Ph-3
A | B | Model | kW | kVAr | kW | kVAr | kW | kVAr
802 | 806 | Y-PQ | 0 | 0 | 30 | 15 | 25 | 14
808 | 810 | Y-I | 0 | 0 | 16 | 8 | 0 | 0
818 | 820 | Y-Z | 34 | 17 | 0 | 0 | 0 | 0
820 | 822 | Y-PQ | 135 | 70 | 0 | 0 | 0 | 0
816 | 824 | D-I | 0 | 0 | 5 | 2 | 0 | 0
824 | 826 | Y-I | 0 | 0 | 40 | 20 | 0 | 0
824 | 828 | Y-PQ | 0 | 0 | 0 | 0 | 4 | 2
828 | 830 | Y-PQ | 7 | 3 | 0 | 0 | 0 | 0
854 | 856 | Y-PQ | 0 | 0 | 4 | 2 | 0 | 0
832 | 858 | D-Z | 7 | 3 | 2 | 1 | 6 | 3
858 | 864 | Y-PQ | 2 | 1 | 0 | 0 | 0 | 0
858 | 834 | D-PQ | 4 | 2 | 15 | 8 | 13 | 7
834 | 860 | D-Z | 16 | 8 | 20 | 10 | 110 | 55
860 | 836 | D-PQ | 30 | 15 | 10 | 6 | 42 | 22
836 | 840 | D-I | 18 | 9 | 22 | 11 | 0 | 0
862 | 838 | Y-PQ | 0 | 0 | 28 | 14 | 0 | 0
842 | 844 | Y-PQ | 9 | 5 | 0 | 0 | 0 | 0
844 | 846 | Y-PQ | 0 | 0 | 25 | 12 | 20 | 11
846 | 848 | Y-PQ | 0 | 0 | 23 | 11 | 0 | 0
Total |  |  | 262 | 133 | 240 | 120 | 220 | 114

## line data
Line Segment Data
Node A | Node B | Length(ft.) | Config.
800 | 802 | 2580 | 300
802 | 806 | 1730 | 300
806 | 808 | 32230 | 300
808 | 810 | 5804 | 303
808 | 812 | 37500 | 300
812 | 814 | 29730 | 300
814 | 850 | 10 | 301
816 | 818 | 1710 | 302
816 | 824 | 10210 | 301
818 | 820 | 48150 | 302
820 | 822 | 13740 | 302
824 | 826 | 3030 | 303
824 | 828 | 840 | 301
828 | 830 | 20440 | 301
830 | 854 | 520 | 301
832 | 858 | 4900 | 301
832 | 888 | 0 | XFM-1
834 | 860 | 2020 | 301
834 | 842 | 280 | 301
836 | 840 | 860 | 301
836 | 862 | 280 | 301
842 | 844 | 1350 | 301
844 | 846 | 3640 | 301
846 | 848 | 530 | 301
850 | 816 | 310 | 301
852 | 832 | 10 | 301
854 | 856 | 23330 | 303
854 | 852 | 36830 | 301
858 | 864 | 1620 | 302
858 | 834 | 5830 | 301
860 | 836 | 2680 | 301
862 | 838 | 4860 | 304
888 | 890 | 10560 | 300

## Regulator Data
Regulator Data
Regulator ID: | 1
Line Segment: | 814 - 850
Location: | 814
Phases: | A - B -C
Connection: | 3-Ph,LG
Monitoring Phase: | A-B-C
Bandwidth: | 2.0 volts
PT Ratio: | 120
Primary CT Rating: | 100
Compensator Settings: | Ph-A | Ph-B | Ph-C
R - Setting: | 2.7 | 2.7 | 2.7
X - Setting: | 1.6 | 1.6 | 1.6
Volltage Level: | 122 | 122 | 122
Regulator ID: | 2
Line Segment: | 852 - 832
Location: | 852
Phases: | A - B -C
Connection: | 3-Ph,LG
Monitoring Phase: | A-B-C
Bandwidth: | 2.0 volts
PT Ratio: | 120
Primary CT Rating: | 100
Compensator Settings: | Ph-A | Ph-B | Ph-C
R - Setting: | 2.5 | 2.5 | 2.5
X - Setting: | 1.5 | 1.5 | 1.5
Volltage Level: | 124 | 124 | 124
*********************************************************************